## Slide 2
İLK KURULUM
MPR-4 Series Network Analyzer Connection Correction Manual
V1 Voltage Cable
(#12 terminal)
V2 Voltage Cable
(#13 terminal)
V3 Voltage Cable
(#14 terminal)
Neutral Connection Cable
(#16 terminal)
Earth Connection Cable
(#15 terminal)
The voltage cables taken from the point to be measured must be connected to the voltage measuring terminal where is on top left of device.
V1, V2, V3 terminal inputs are used for measuring the voltage of the three phases.
Voltage Terminal Connection
The voltage cable from phase 2 is connected to V2 (2nd input) #13 terminal,
The voltage cable from phase 1 is connected to V1 (first input) #12 terminal,
ATTENTION! The earth-neutral voltage terminal (#15) and the neutral terminal (#16) shall be connected according to the connection type.
Neutral is connected to #16 terminal.
#15 terminal is used for earth-neutral voltage measurement.
The voltage cable from phase 3 is connected to V3 (3rd input) #14 terminal,

## Slide 3
İLK KURULUM
Preferably Phase Connection
(#9 terminal)
Preferably Neutral Connection
(#11 terminal)
The red terminal located in the upper right corner of the device is the supply terminal. The supply voltage connection, which may differ according to the product version, is made from this terminal.
As can be fed from one of the measuring terminals or it is preferred to feed it though a separte fuse.
#9 and #11 terminals are connected to the phase and neutral from the grid circuit, the order of connection is not important.
ATTENTION! For DC models, it is important to connect (+) to # 9 and (-) to #11 terminal.
MPR-4 Series Network Analyzer Connection Correction Manual
Supply Terminal Connection

## Slide 4
K1 and L1 cable
of CT1
(#1 and #2 terminals)
K2 and L2 cable
of CT2
(#3 and #4 terminals)
K3 and L3 cable
of CT3
(#5 and #6 terminals)
K4 and L4 cable of CT4
(#7 and #8 terminals)
Secondary K - L cables of current transformers (K1-L1, K2-L2 and K3-L3) are connected to the current terminal where is on top left of device.
K1 cable from 1st Current Transformer is connected to 1st terminal, L1 cable is connected to 2nd terminal,
ATTENTION! If you want to measure neutral current, you can connect the leads from current transformer connected to the neutral to #7 and #8 terminals.
K3 cable from 3rd Current Transformer is connected to 5th, L3 cable is connected to 6th terminal,
K2 cable from 2nd Current Transformer is connected to 3rd, L2 cable is connected to 4th terminal,
MPR-4 Series Network Analyzer Connection Correction Manual
Current Terminal Connection

## Slide 5
MPR-4 Series Network Analyzer Connection Correction Manual
İLK KURULUM
«Ground»
(#17 terminal)
«B»
(#18 terminal)
«A»
(#19 terminal)
«TR»
(#20 terminal)
If your device is a version with communication, cables from the modem or other communication devices are connected to the RS-485 port where is on bottom right of device.
B cable is connected to #18 (2nd terminal),
Ground cable is connected to #17 (1st terminal),
ATTENTION! The important point here is to make the connection in Ground, B, A and TR.
TR cable is connected to #20 (4th terminal),
A cable is connected to #19 (3rd terminal),
Congratulations, you have successfully completed the installation.
Communication Terminal Connection

## Slide 6: Bağlantı Kontrolü ve Bağlantı Düzeltme Adımları

## Slide 7
Step 4
If the phase sequence icon is active, de-energize the device and follow the steps.
Step 2
Verify that the voltage values ​​are at least 100V.
Step 1
Press the “V I F” button on the device to voltage display.
Step 3
Check that the phase sequence icon is on the display.
ATTENTION!
If the phase sequence icon is not active, go to step 7.
MPR-4 Series Network Analyzer Connection Correction Manual

## Slide 8
Step 7
Ensure that a load is activated in the system.
Step 6
Verify that the phase sequence error is corrected (icon is not active) by energizing the device.
Step 5
Change the connections V2 and V3.
MPR-4 Series Network Analyzer Connection Correction Manual

## Slide 9
Step 8
Press the “P PF” button on the device to cosfi display.
Confirm that the values ​​on this screen are stable.
If the values ​​are unstable, allow more load to the system.
MPR-4 Series Network Analyzer Connection Correction Manual

## Slide 10
Energizing the device and return to step 8 .
Step 9
Check the values ​​on the Cos fi screen to see if it is bigger than 0.87.
Scenario 1
If no value is bigger than 0.87,
de-energized the device and move the voltage connections to one right.
MPR-4 Series Network Analyzer Connection Correction Manual

## Slide 11
Scenario 2
If the value of phase 1 is bigger than 0.87 and the others are smaller;
De-energized the device and replace the current connections of phase 2 and phase 3.
Return to Step 8 after energizing the device.
Scenario 4
If the value of phase 3 is bigger than 0.87 and the others are smaller;
De-energized the device and replace the current connections of phases 1 and 2.
Return to Step 8 after energizing the device.
Scenario 3
If the value of phase 2 is bigger than 0.87 and the others are smaller;
De-energized the device and replace the current connections of phases 1 and 1.
Return to Step 8 after energizing the device.
Senaryo5
If 2 or 3 values ​​are bigger than 0.87, go to Step 10.
MPR-4 Series Network Analyzer Connection Correction Manual

## Slide 12
NOTE: If there is not any negative value, connections are correct.
Step 10
Press the “P PF” button on the device to active power display.
Step 11
Check the values ​​and note the phases which is negative value (starting with “- “).
MPR-4 Series Network Analyzer Connection Correction Manual

## Slide 13
Energizing the device and return to step 10 .
Scenario 1
If the value of phase 1 is negative;
De-energized the device and replace the current connections of phase 1 and phase 2 (K1-L1).
MPR-4 Series Network Analyzer Connection Correction Manual

## Slide 14
Scenario 2
If the value of phase 2 is negative;
De-energized the device and replace the current connections of phase 3 and phase 4 (K2-L2).
MPR-4 Series Network Analyzer Connection Correction Manual
Energizing the device and return to step 10 .

## Slide 15
Scenario 3
If the value of phase 3 is negative;
De-energized the device and replace the current connections of phase 5 and phase 6 (K3-L3) .
MPR-4 Series Network Analyzer Connection Correction Manual
Energizing the device and return to step 10 .